## Sizing
Hoima-Kigolobya Solar Sizing Third draft
No. | Appliance | Quantity | Unit | Rating (watts) | Total watts | operating hour | Watt hours (Wh)
1 | Cooking, pressure cooker: Main house one, Kitchen | 2 | pcs | 1000 | 2000 | 3 | 6000
2 | Cooking, Air fryerr: Main house one, Kitchen | 2 | pcs | 1500 | 3000 | 2 | 6000
3 | Cooking, Induction cookerr: Main house one, Kitchen | 2 | pcs | 2000 | 4000 | 2 | 8000
4 | Heating , Pacoratorr: Main house one, Kitchen | 2 | pcs | 2000 | 4000 | 1 | 4000
5 | Flat iron; main House one | 1 | pcs | 2000 | 2000 | 1 | 2000
6 | Fridge; r: Main house one, Kitchen | 2 | pcs | 800 | 1600 | 12 | 19200
7 | Fridge; Laboratory | 1 | pcs | 1200 | 1200 | 24 | 28800
8 | Blender : Main house one, Kitchen | 2 | pcs | 800 | 1600 | 1 | 1600
9 | TV set : Main house one, Kitchen | 2 | Set | 800 | 1600 | 6 | 9600
10 | AC: Main house one, Office, Laboratory | 3 | pcs | 2000 | 6000 | 2 | 12000
11 | Fan: House 2,3, 5 $ kichen | 4 | pcs | 85 | 340 | 3 | 1020
12 | Mosquito Repelents; Hall houses plus kitchen | 7 | pcs | 5 | 35 | 12 | 420
13 | Lihgts; All houses | 12 | pcs | 6 | 72 | 12 | 864
14 | Lihgts; Outside wall mount on All houses | 12 | pcs | 12 | 144 | 12 | 1728
15 | Lights; outside Toilet | 4 | pcs | 5 | 20 | 12 | 240
16 | Lights; Inside Toilet | 4 | pcs | 5 | 20 | 3 | 60
17 | Fan; Inside Toilet | 4 | pcs | 16 | 64 | 3 | 192
18 | Lights; Security on pole | 10 | pcs | 100 | 1000 | 12 | 12000
19 | Desktop computer set, Laboratory | 2 | pcs | 300 | 600 | 8 | 4800
20 | Desktop computer set, Office | 3 | pcs | 300 | 900 | 6 | 5400
21 | Laptops | 2 | pcs | 65 | 130 | 3 | 390
22 | Spot ligts; Kitchen | 10 | pcs | 3 | 30 | 8 | 240
23 | LED string lights; Kitchen | 3 | pcs | 12 | 36 | 8 | 288
24 | Surver computer | 1 | pcs | 95 | 95 | 24 | 2280
25 | Routers | 1 | pcs | 5 | 5 | 24 | 120 | final sizing:
26 | Acess point Router | 2 | pcs | 10 | 20 | 24 | 480
27 | Printer; Office | 1 | pcs | 800 | 800 | 3 | 2400 |  | Panel size (W) | battery (Ah) | charge cantroller (A) | inverter (W)
28 | Camera | 6 | pcs | 5 | 30 | 24 | 720 | calculated | 33902 | 3611.7187 | 990 | 45570.36
29 | DVR | 1 | pcs | 17 | 17 | 24 | 408 | selected | 33000 | 800 | 100 | 3000
30 | Monitor | 1 | pcs | 25 | 25 | 24 | 600 |  | 6 of 450w | 4 of 200Ah | Inverter embeded | High frequency
31 | Steriizer; Laboratory | 1 | pcs | 1500 | 1500 | 2 | 3000
32 | Juicer/Toster; Kitchen | 1 | pcs | 1500 | 1500 | 2 | 3000
33 | phone charging | 8 | pcs | 5 | 40 | 6 | 240
34 | Un calculated load | 1 | pcs | 100 | 100 | 6 | 600 | coments
Totals |  |  |  |  | 34523 |  | 138690
New totals (to be used in calculations) |  |  |  |  | 37975.3 |  | 152559
fixed data for system calculation
System voltage SV | Peak sunhour PSH | Days of autonomy DOA |  | Depth of descharg DOD | Factor of safty FOS | Total V of a 24v pannel | System efficiency
48 | 5 | 1 |  | 0.8 | 1.2 | 40 | 0.9
|  |  |  | 0.8 |  |  | 0.9
o

## Quotation
Hoima-Kigolobya Solar Sizing Third draft
No. | Item | Description | Quantity | Unit | Unit Rate (UGX) | Amount (UGX)
1 | Storage Battery | Lithium Battery, 48V, 350AH, 17.5KWh Recommended Output Power=10000W (6000cycles with DOD80%, Connected up to 6 in Parallel, communication with FelicitySolar Inverter/4G Module) | 2 | pcs | 9500000 | 19000000
2 | Solar PV panels | 550W, Mono-Half Cut VOC=51.1V, VMP=42.6V, ISC=13.6A, IMP=12.9A 2279*1134*35mm, 4㎡PV Cable=0.9M, MC4 | 18 | pcs | 550000 | 9900000
3 | Battery/ssystem protection | metallic smooth fabrication, painting and ground protetion pads | 1 | pc | 800000 | 800000
4 | Dc cables | UV DC cable 16sqmm Single core multstranded 50 Black and 50 blue | 100 | Mtr | 12000 | 1200000
5 |  | UV DC cable 35sqmm single core multstranded 20 red and 20 blue | 40 | Mtr | 26000 | 1040000
6 | Ac cables | single core 4sqmm Red, Black and Yellow-green | 50 | Mtr | 4200 | 210000
7 |  | Under ground 2.2mm 4 core | 180 | mtr | 22000 | 3960000
8 | inverter | 5KVA/4000W, 48V, 50/60HZ Communication function with Lithium Battery/Wifi/4G Module (Built-in MPPT Charger 120A Max, PV Input: Max.6600W/60~195V) | 3 | pc | 4000000 | 12000000
9 | Trunking | Two compatiments with accessories | 1 | set | 170000 | 170000
10 | Cable lugs | 16sqmm copper cable lugs | 16 | pcs | 2000 | 32000
11 |  | 35sqmm copper cable lugs | 10 | pcs | 3500 | 35000
12 | cable ties | black 200sqmm | 2 | pc | 32000 | 64000
13 | screws | self taping star 3 inch screws | 1 | pct | 28000 | 28000
14 |  | self taping star 1.5 inch | 1 | pct | 23000 | 23000
15 | Breakers | Ac circuit breakers | 7 | pcs | 35000 | 245000
16 |  | 100A Dc circuit breaker and their enclosure | 6 | pcs | 120000 | 720000
17 | Board | Water proof board with indicator set | 1 | pc | 270000 | 270000
18 | Switch | Automatic voltage switcher (AVS-30A) | 3 | pc | 145000 | 435000
19 |  | Emergency maual change over 32A three phase | 1 | pc | 270000 | 270000
20 | Wifi Dongle | Wifi Plug Pro for Wireless Mornitoring Solar Energy System Android/IOS APP, RJ45 Communication Port | 1 | pc | 190000 | 190000
21 | Panel stands | Non corrosive panel stands, alminium rays/Stands | 1 | set | 4000000 | 4000000
[5 empty] | Cost of materials | 54592000
[5 empty] | Transport | 400000
|  | Consultancy,installation and commisioning Fees= 10% of material cost |  |  |  | 5459200
[5 empty] | Grand Total | 60451200
1,700 USD