## Sizing
Ntinda solar sizing for Joan
No. | Appliance | Quantity | Unit | Rating (watts) | Total watts | operating hour | Watt hours (Wh) | Group (Wh)
AIRTEL SHOP
1 | Pannel lights | 13 | pcs | 18 | 234 | 3 | 702 | 6306
2 | Spot lights | 13 | pcs | 6 | 78 | 3 | 234
3 | Television | 2 | pcs | 65 | 130 | 3 | 390
4 | Desktop | 7 | pcs | 95 | 665 | 3 | 1995
5 | Laptops | 4 | pcs | 65 | 260 | 3 | 780
6 | Printers | 2 | pcs | 80 | 160 | 3 | 480
7 | Token machine | 1 | pcs | 300 | 300 | 3 | 900
8 | Money counting machine | 3 | pcs | 80 | 240 | 3 | 720
9 | Camera systems | 1 | set | 35 | 35 | 3 | 105
[5 empty] | 0 |  | 0
10 | PHARMACY |  |  |  | 0 |  | 0
11 | Pannel lights | 8 | pcs | 18 | 144 | 3 | 432 | 5745
12 | LED flourescent lights | 8 | pcs | 18 | 144 | 3 | 432
13 | ceiling fan | 1 | pcs | 24 | 24 | 3 | 72
14 | Wall fan | 1 | pcs | 18 | 18 | 3 | 54
15 | Monitor & DVR | 1 | set | 35 | 35 | 3 | 105
16 | Fridge |  |  |  | 0 | 3 | 0
17 | Sign post | 1 | pcs | 50 | 50 | 3 | 150
18 | Steriizer | 1 | pcs | 1500 | 1500 | 3 | 4500
| UMOJA |  |  |  | 0 |  | 0
19 | Rescess spot lights | 15 | pcs | 15 | 225 | 3 | 675 | 6576
20 | Surface spot lights | 24 | pcs | 30 | 720 | 3 | 2160
21 | LED flourescent lights | 24 | pcs | 18 | 432 | 3 | 1296
22 | Monitor | 1 | pcs | 100 | 100 | 3 | 300
23 | DVR | 1 | pcs | 35 | 35 | 3 | 105
24 | Speaker system | 4 | pcs | 70 | 280 | 3 | 840
25 | Television | 1 | pcs | 80 | 80 | 3 | 240
26 | LED flourescent lights | 4 | pcs | 30 | 120 | 3 | 360
27 | Flood lights | 2 | pcs | 50 | 100 | 3 | 300
28 | Sign post lights | 2 | pcs | 50 | 100 | 3 | 300
| OFFICES |  |  |  | 0 |  | 0
29 | Laptops | 10 | Pcs | 65 | 650 | 3 | 1950 | 2502
30 | Pannel lights | 2 | Pcs | 28 | 56 | 3 | 168
31 | Normal lights | 2 | Pcs | 18 | 36 | 3 | 108
32 | Pannel lights | 1 | Pcs | 12 | 12 | 3 | 36
33 | Monitor & router | 1 | Pcs | 80 | 80 | 3 | 240
[5 empty] | 0 |  | 0
34 | POWER HOUSE |  |  |  | 0 |  | 0
35 | Lights | 3 | pcs | 12 | 36 | 3 | 108 | 108
[5 empty] | 0 |  | 0
36 | MAIN CHURCH |  |  |  | 0 |  | 0
37 | Pannel lights | 8 | pcs | 18 | 144 | 3 | 432 | 732
38 | Flood lights | 1 | pcs | 100 | 100 | 3 | 300
[5 empty] | 0 |  | 0
39 | SUNDAY SCHOOL CHURCH |  |  |  | 0 |  | 0
40 | Normal lights | 4 | pcs | 18 | 72 | 3 | 216 | 216
[5 empty] | 0 |  | 0
41 | EMPTY ROOM |  |  |  | 0 |  | 0
42 | Pannel lights | 4 | pcs | 28 | 112 | 3 | 336 | 1152
43 | Normal lights | 4 | pcs | 18 | 72 | 3 | 216
44 | Buffer load | 1 | set | 200 | 200 | 3 | 600
[5 empty] | 0 |  | 0
45 | OUTSIDE & LOBBY |  |  |  | 0 |  | 0
46 | Pannel lights | 9 | pcs | 24 | 216 | 3 | 648 | 1398
47 | Security wall lights | 5 | pcs | 50 | 250 | 3 | 750
| Land Load |  |  |  | 0 |  | 0
48 | Camera | 6 | pcs | 5 | 30 | 3 | 90 | 816
49 | DVR | 1 | pcs | 17 | 17 | 3 | 51 |  | final sizing:
50 | Monitor | 1 | pcs | 25 | 25 | 3 | 75 |  |  | Panel size (W) | battery (Ah) | charge cantroller (A) | inverter (W)
51 | phone charging | 20 | pcs | 5 | 100 | 3 | 300 |  | calculated | 6245.8 | 665.3906 | #VALUE! | 11242.44
52 | Un calculated load | 1 | pcs | 100 | 100 | 3 | 300 |  | selected | 7200Wp | 17.5KWh | 120A | 10KVA/8000W
Totals |  |  |  |  | 8517 |  | 25551 |  |  | 16 of 450w | 2 of 350Ah | Inverter embeded | High frequency
New totals (to be used in calculations) |  |  |  |  | 9368.7 |  | 28106.1 |  | coments
fixed data for system calculation
System voltage SV | Peak sunhour PSH | Days of autonomy DOA |  | Depth of descharg DOD | Factor of safty FOS | Total V of a 24v pannel | System efficiency
48 | 5 | 1 |  | 0.8 | 1.2 | 40 | 0.9
|  |  |  | 0.8 |  |  | 0.9

## Quotation
No. | Item | Description | Quantity | Unit | Unit Rate (UGX) | Amount (UGX)
1 | Storage Battery | Lithium Battery, 48V, 350AH, 17.5KWh Recommended Output Power=10000W (6000cycles with DOD80%, Connected up to 6 in Parallel, communication with FelicitySolar Inverter/4G Module) | 2 | pcs | 9500000 | 19000000
2 | Solar PV panels | 450W, Mono-Half Cut VOC=47V, VMP=40.1V, ISC=11.9A, IMP=11.25A 1960*1060*35mm, 4㎡PV Cable=0.9M, MC4 | 16 | pcs | 450000 | 7200000
3 | Battery protection | metallic smooth fabrication, painting and ground protetion pads | 1 | pc | 850000 | 850000
4 | Dc cables | UV DC cable 16sqmm Single core multstranded Black and blue | 80 | Mtr | 12000 | 960000
5 |  | UV DC cable 35sqmm single core multstranded red and blue | 30 | Mtr | 26000 | 780000
6 | Ac cables | single core 4sqmm Red, Black and Yellow-green | 50 | Mtr | 4200 | 210000
7 |  | Airtel 6mm Twin with Earth | 50 | Mtr | 8000 | 400000
8 |  | Pharmacy 4mm Twin with Earth | 40 | Mtr | 5500 | 220000
9 |  | Umoja 4mm Twin with Earth | 30 | Mtr | 5500 | 165000
10 |  | Office 4mm Twin with Earth | 40 | Mtr | 5500 | 220000
11 |  | Church 4mm Twin with Earth | 25 | Mtr | 5500 | 137500
12 |  | Empty room 4mm Twin with Earth | 20 | Mtr | 5500 | 110000
13 | inverter | 10KVA/8000W, 48V, 50/60HZ Communication function with Lithium Battery/Wifi/4G Module (Built-in MPPT Charger 120A Max, PV Input: Max.6600W/60~195V) (Parallel Unit up to 6PCS, Single/Three Phase) | 1 | pc | 5500000 | 5500000
14 | MPPT Charge controller | 120A, 12V/24V/48V, PV Max.=200V, Li Activated Function Max Input Power: 12V-1650W, 24V-3300W, 48V-6600W | 1 | pc | 1200000 | 1200000
15 | Trunking | Two compatiments with accessories | 1 | set | 170000 | 170000
16 | Cable lugs | 16sqmm copper cable lugs | 16 | pcs | 2000 | 32000
17 |  | 35sqmm copper cable lugs | 10 | pcs | 3500 | 35000
18 | cable ties | black 200sqmm | 2 | pc | 32000 | 64000
19 | screws | self taping star 3 inch screws | 1 | pct | 28000 | 28000
20 |  | self taping star 1.5 inch | 1 | pct | 23000 | 23000
21 | Breakers | Ac circuit breakers | 7 | pcs | 35000 | 245000
22 |  | 100A Dc circuit breaker and their enclosure | 8 | pcs | 50000 | 400000
23 | Board | Water proof board with indicator set | 1 | pc | 270000 | 270000
24 | Switch | Automatic voltage switcher (AVS-30A) | 3 | pc | 145000 | 435000
25 |  | Emergency maual change over 63A three phase | 1 | pc | 680000 | 680000
26 | Wifi Dongle | Wifi Plug Pro for Wireless Mornitoring Solar Energy System Android/IOS APP, RJ45 Communication Port | 1 | pc | 190000 | 190000
27 | Panel stands | Non corrosive panel stands, alminium rays/Stands | 4 | sets | 750000 | 3000000
[5 empty] | Cost of materials | 42524500
[5 empty] | Transport | 300000
|  | Consultancy,installation and commisioning Fees= 10% of material cost |  |  |  | 4252450
[5 empty] | Grand Total | 47076950